DIVISION 23 8313 Radiant Electric Heating Cables

GUTTERMELT ROOF / GUTTER HEAT TRACE SYSTEM MINERAL INSULATED

PART 1 - GENERAL

  - SUMMARY

- Includes But Not Limited To:

  - Furnish a complete system of heating cables, components, and controls, specifically for keeping water drainage paths clear and to avoid ice dams on roof eaves, gutters, and downspouts.

- Related Sections:

      - Section 073100 - Shingles and Shake: Installation coordination with roofing material and details

      - Section 073200 - Roof Tiles: Installation coordination with roofing material and details.

      - Section 074100 - Roof Panels: Installation coordination with roofing material and details.

      - Section 075000 – Membrane Roofing: Installation coordination with gutter material and details.

      - Section 076000 – Flashing and Sheet Metal: Installation coordination with gutter material and details.

      - Section 077000 – Roof and Wall Specialties and Accessories: Installation coordination with gutter material and details.

      - Section 260600 – Schedules for Electrical: Materials and installation of wiring and electrical power source.

1.2   SYSTEM DESCRIPTION

  - The system shall consist of all equipment and materials to keep water drainage paths clear and/or avoid ice dams on roof eaves, gutters, and downspouts.

  - The area covered and heat density (measured by Watts or BTU equivalent) per linear foot of heating element or square foot of area for each Heatizon System product are determined by the heat output and the spacing between adjacent runs of heating element.  See manufacturer’s installation instructions for more detailed information.

  - ELECTRICAL CODES AND STANDARDS

  - The entire design and installation of the Heatizon GutterMelt® MI Cable System shall comply with the Manufacture’s Installation Manual.

  - National Electrical Code (NEC) for US installations; Canadian Standards Association (CSA) for Canadian Installations. (Current Editions).

  - Requirements of the "Authority Having Jurisdiction".

  - All GutterMelt® MI Cable Heaters shall be approved to CSA and UL Standards as part of the system for keeping water drainage paths clear and to avoid ice dams on roof eaves, gutters, and downspouts.

    - Self-regulating cables are not acceptable for this application.

    - Cables that are not copper shielded are not acceptable for this application.

    - Cables where conductors are not insulated by fiberglass are not acceptable for this application.

  - Enclosures shall be rated NEMA 4X to prevent water ingress and corrosion.

- SUBMITTALS

  - Product Data:

    - Submit manufacturer’s technical product data and written installation instructions for the GutterMelt® MI cable system.

  - Shop Drawings:

    - At architect’s request, submit drawings showing layout of system relay or contactor panel, activation device, grounding connections, and heating cables required to provide complete operating system.  Including the following:

      - Locations for activation devices.

      - Locations of relay panel, contactor panel, junction boxes, feeder wires, and load wires.

      - Circuit feeder runs from relay or contactor panel / junction box to heating element connection points.

      - Connection points between circuit feeders and heating element.

      - Wiring between relay panel and activation device.

      - Location of aerial or roof and gutter temperature moisture sensor(s).

      - Differentiate between:

        - Control wiring.

        - Heating element.

        - Cold Lead.

        - Branch-circuit wiring.

      - Differentiate between zones of heating element.

  - Operation and Maintenance Data:

1.	Submit manufacturer’s written maintenance and operation instructions for system.

  - Warranty:

    - Submit copy of system manufacturer’s standard warranty for system.

- QUALITY ASSURANCE

  - Manufacturer’s Qualifications:

    - Firm regularly engaged in manufacturing of electric cable heating elements, of type, sizes, and ratings required, whose products have been in satisfactory use in similar services for not less than five years.

  - Installer Qualifications:

    - Licensed Electrical Contractor with a minimum of two years successful certified experience installing projects utilizing electric heating cable systems equal to systems specified in this section.

  - Regulatory Requirements:

    - Comply with applicable local electrical code requirements of local authorities having jurisdiction.

    - Provide products that are listed recognized and labeled by Nationally Recognized Testing Laboratory (NRTL) that includes, but not limited to :

      - ETL subsidiary of Intertek.

      - Canadian Standards Association (CSA).

      - Underwriters Laboratories (UL).

    - Conform to requirements of “Standard for Safety Electric Space Heating Cables” (UL – 1673, 3rd Edition, dated September 13, 2010)

    - Conform to requirements of “Roof and Gutter De-icing Cable Units Issue Number 4” (UL Subject 1588, dated May 24, 2002)

    - Conform to “Requirements for Electrical Resistance Heating Cables and Heating Device Sets” (CSA – 22.2, No 130, 3rd Edition, dated January 2008)

- DELIVERY, STORAGE AND HANDLING

  - Deliver, store, and handle in accordance with manufacturer’s written instructions.  Store materials in dry indoor location off the ground.

  - Remove damaged materials from job site and replace with new at no additional cost to owner.

- WARRANTY

  - Provide the Manufacturer Standards with following requirements:

    - GutterMelt® MI Cable heating element:			Ten year

    - Relay Panel, Contactor Panel, and Activation devices:	One year

PART 2 - PRODUCTS

- MANUFACTURER

  - Approved Manufacturers:

    - Heatizon Systems, 4137 South 500 West, Murray, Utah 84123 (888) 293-1232  www.heatizon.com – info@heatizon.com

  - Substitutions: Not Permitted.

- COMPONENTS

  - Heating Element

    - GutterMelt® MI Cable shall be supplied by Heatizon Systems (Tel: 888-239-1232, Fax: 801-293-3077)

    - Shall be fiberglass insulated, with a copper or resistance alloy conductor and a seamless copper sheath.

    - Constructed in such a manner that no combustible materials are allowed between the resistance alloy conductor and outer metal sheath.

    - All heater core materials shall be inorganic and will not deteriorate with age.

    - Jacketed with high density polyethylene (HDPE) to further resist corrosion.

    - Pre-fabricated by Heatizon Systems to the length required and shall not be altered in the field. The heated section shall be joined to a PVC jacketed copper sheath cold lead section by a pre-fabricated joint by Heatizon Systems.

    - Cold lead shall be standard twenty five feet long or a predetermined custom length and can be extended at a junction box with circuit feeders.

    - To ensure maximum heating rate, heat output shall not self regulate (decrease as the ambient temperature increases).

    - The heating cable shall operate on line voltages of (select: 120, 208, 220, 240, 277, 347, 480, or 600) volts.

  - Relay Control Panel or Contactor Panel

    - Heatizon M330 Relay Panel Control Series

a. 	M330 Series Relay Panel accommodating 2, 4, 6, or  8, 30A resistive poles with manual activation switches.

b.	M330G Series Relay Panel accommodating 2, 4, 6, or  8, 30A resistive poles with built in Ground Fault Equipment Protection and manual activation switches.

c.	M330G-40 Series Relay Panel accommodating 2, 4, 6, or  8, 40A resistive poles with built in Ground Fault Equipment Protection and manual activation switches.

d.	M330-50 Series Relay Panel accommodating 2, 4, 6, or  8, 50A resistive poles with manual activation switches

2.	Heatizon M530 Contactor Panel Series

a. 	M530-1 Contactor Panel accommodating 4, 50A resistive poles.

b. 	M530-2 Contactor Panel accommodating 8, 50A resistive poles.

c. 	M530-3 Contactor Panel accommodating 12, 50A resistive poles.

d. 	M530-4 Contactor Panel accommodating 16, 50A resistive poles.

  - Activation

    - All GutterMelt® MI Cable circuits shall be activated by a Heatizon Systems approved activator for GutterMelt® MI Cable:

      - Manual Control:

- The system shall be controlled by a switch, either directly or through an appropriate contactor.

      - Snow Switch Control:

- An automatic snow/ice sensor (preferred) which detects precipitation occurring at temperatures below 38° F (4 ° C). Example Models: M332 / M326A / M326ARS / M435

      - Thermostatic Control:

- The system shall be controlled by an adjustable ambient sensing thermostat.

      - Multiple Circuits for Control, Monitoring and Power Distribution:

- Where the rating of the activator would be exceeded, it shall be used in conjunction with a Heatizon Relay Control Panel (M330 Series) or Contactor Panel (M530 Series) for activation of multiple heater circuits.

PART 3 – EXECUTION

  - EXAMINATION

    - Examine areas where heating element is to be installed for proper installation, cleanliness, and conditions that may hinder successful installation of GutterMelt® MI cable system.

    - Notify Contractor in writing of items needing correction.

    - Do not install GutterMelt® MI cable system until faulty conditions are corrected.

  - INSTALLATION

  - Interface with Other Work:

      - Coordinate installation of GutterMelt® MI cable system with appropriate sections of Division 26 Electrical.

- The current Heatizon GutterMelt® MI Cable Installation Manual shall be considered as part of this specification.

- The heating cable shall be laid in gutters; shall be suspended in downspouts either as a loop or a single length and held in place by a downspout hanger; and shall be attached to the roof using the roof clips.

- All terminations shall be protected from the weather and from physical damage and bonded to the system ground.

- The heating cable shall be protected from damage and installed according to manufacturer’s instructions.

- Any field alternations or deviations shall proceed only after authorization has been issued by engineer. All changes shall be accurately recorded by the contractor and shall be turned over to the engineer upon completion of the heating system scope of work.

- FIELD QUALITY CONTROL

  - Testing as directed by system manufacturer.

    - Field testing of insulation resistance and continuity of the units shall be carried out with a 500VDC Megohmmeter insulation tester and recorded by the Electrical Contractor.

    - Testing shall be performed by the Electrical Contractor done in the following order:

      - Prior to Installation of GutterMelt® MI Heating Cable (when removed from package).

      - After Installation of GutterMelt® MI Heating Cable on roof, gutters, drains, or downspouts.

- RESISTANTANCE RECORDING

  - Insulation resistance shall be consistently not less than 20 megohms during each test.

  - A complete system startup shall be performed to verify successful operation.

  - Resistance readings shall be recorded in the GutterMelt® MI Cable Design and Installation Manual

- DEMOSTRATION

  - Provide adequate demonstration and training to Owner in operation and maintenance of system.

END OF SECTION